# MOOSE 1000 – 1080 PANELS

ADDING 4 WIRE SMOKE DETECTOR(S) WITH TONER(S)

SMOKE DETECTORS  - SYSTEM SENSOR – 4WTA-B

1- STOCK NEEDED BESIDES SMOKE DETECTORS:

1- SYSTEM SENSOR  RRS  MODULE

1- ALTRONIX  RB610  RELAY (OR EQUIVALENT)

1- MOOSE 4 WIRE (KEYPAD STYLE CONNECTOR)

2- WIRING:

- POWER DOWN CONTROL

- MOUNT RRS MODULE ON CABINET

- MOUNT RELAY IN CABINET

- INSTALL MOOSE 4 WIRE CONNECTOR ON THE UPPER

PART OF THE BOARD – (J2 OUTPUT JACK)  RED WIRE

SHOULD BE ON THE LEFT.

- RRS  MODULE WIRING:

- PURPLE WIRE – CONNECT TO -RELAY  “NO” TERM.

- YELLOW WIRE-CONNECT TO –CONTROL TERM “4”

- ORANGE WIRE- CONNECT TO CONTROL TERM  “5”

- BLACK  WIRE  - CONNECT TO CONTROL TERM  “5”

- RED        WIRE  - CONNECT TO CONTROL TERM  “6”

- BROWN WIRE -  CONNECT TO “1 +in” – 1ST SMOKE  DET.

- WHITE   WIRE-   CONNECT TO “3 –in/out” – 1st SMOKE DET

( FOLLOW SMOKE DET WIRING DIAGRAM FOR ADDITIONAL

SMOKE DETECTORS )

- RELAY WIRING:

-  PLACE A JUMPER BETWEEN THE  ( +  ) AND THE “C” TERM

- BLACK WIRE OF “J2” OUTPUT CONN  TO ( -- )

- GREEN WIRE OF “J2” OUTPUT CONN  TO ( + )

- ( PURPLE WIRE SHOULD BE ON “NO” { FROM RRS MOD} )

- CONTROL- ZONE WIRING/ PROGRAMMING:

- WIRE SMOKE DETECTORS TO THE ZONE

-  PROGRAMMING NOTES:

-  PROGRAM OUTPUT NUMBER 3 (GREEN WIRE OF J2)

### FOR FIRE

- PROGRAM LOCATION IS                  034

- PROGRAM VALUE TO ENTER IS    2

TERMINAL “4” SHOUL BE FACTORY  PRGRAMMED AS  112

(SWITCHED POWER FOR SMOKE DET)….IF NOT…. YOU

NEED TO PROGRAM  FUNCTION LOCATION  033  WITH

A VALUE OF   112

# MOOSE 1000 – 1080 PANELS

ADDING 4 WIRE SMOKE DETECTOR(S) WITH TONER(S)

## SMOKE DETECTORS  - SYSTEM SENSOR – 4WTA-B

3- POWER UP CONTROL

4- CHECK SMOKE DETECTORS FOR OPERATION

5- TEST SMOKE DETECTORS.  RELAY SHOULD ACTIVATE AND

ALL SMOKE DETECTOR SOUNDERS SHOULD ACTIVATE.

6- SILENCE AND RESET

7- RESET SMOKE POWER BY HOLDING DOWN KEYPAD BUTTON  “7”

FOR AT LEAST 4 SECONDS.

8- TO ADD A STROBE (MAC FARMS) YOU CAN WIRE THE STROBE  ( + )

THE RELAY’S “NC” TERM ( PURPLE WIRE TO RRS MODULE)

WIRE THE STROBE ( - ) TO THE RELAY’S( - )  TERMINAL