ENGINEERING SPECIFICATION

50-POINT INTELLIGENT COMMUNICATING FIRE DETECTION SYSTEM

### Specification prepared for :________________________________________

# PART 1.0 - GENERAL

1.1.	DESCRIPTION:

A.	This section of the specification includes the furnishing, installation, connection and testing of the microprocessor controlled, intelligent reporting fire alarm equipment required to form a complete, operative, coordinated system. It shall include, but not be limited to, alarm initiating devices, alarm notification appliances, Fire Alarm Control Panel (FACP), auxiliary control devices, annunciators, and wiring as shown on the drawings and specified herein.

B.	The fire alarm system shall comply with requirements of NFPA Standard No. 72 for Local Protected Premises Signaling Systems except as modified and supplemented by this specification. The system field wiring shall be supervised either electrically or by software-directed polling of field devices.

1.	The Secondary Power Source of the fire alarm control panel will be capable of providing at least 24 hours of backup power with the ability to sustain 5 minutes in alarm at the end of the backup period.

C.	The FACP and peripheral devices shall be manufactured 100% by a single U.S. manufacturer (or division thereof).

D.	Underwriters Laboratories Inc. (UL) - USA:

No. 38 	Manually Actuated Signaling Boxes

No. 50 	Cabinets and Boxes

# No. 864 	Control Units for Fire Protective Signaling Systems

No. 268	Smoke Detectors for Fire Protective Signaling Systems

No. 268A	Smoke Detectors for Duct Applications

No. 346	Waterflow Indicators for Fire Protective Signaling Systems

No. 464 	Audible Signaling Appliances

No. 521	Heat Detectors for Fire Protective Signaling Systems

No. 1971 	Visual Notification Appliances

1.2.	SCOPE:

A.	An intelligent, microprocessor-controlled, fire alarm detection system shall be installed in accordance to the project specifications and drawings.

B.	Basic Performance:

1.	Alarm, trouble and supervisory signals from all intelligent reporting devices shall be encoded on NFPA Style 4 (Class B) Signaling Line Circuits (SLC).

2.	Initiation Device Circuits (IDC) shall be wired Class B (NFPA Style B) as part of an addressable device connected by the SLC Circuit.

3.	Notification Appliance Circuits (NAC) shall be wired Class B (NFPA Style Y) as part of an addressable device connected by the SLC Circuit.

4.	All circuits shall be power-limited, per 1995 UL864 requirements.

5.	A single ground fault or open circuit on the system Signaling Line Circuit shall not cause system malfunction, loss of operating power or the ability to report an alarm.

6.	Alarm signals arriving at the main FACP shall not be lost following a primary power failure or outage of any kind until the alarm signal is processed and recorded.

C.	BASIC SYSTEM FUNCTIONAL OPERATION

When a fire alarm condition is detected and reported by one of the system initiating devices, the following functions shall immediately occur:

1.	The system Alarm LED on the FACP shall flash.

2.	A local sounder with the control panel shall sound.

3.	A backlit 80-character LCD display on the FACP shall indicate all information associated with the fire alarm condition, including the type of alarm point and its location within the protected premises.

4.	In response to a fire alarm condition, the system will process all control programming and activate all system outputs (alarm notification appliances and/or relays) associated with the point(s) in alarm

1.3.	SUBMITTALS

A.	General:

1.	Two copies of all submittals shall be submitted to the Architect/Engineer for review.

2.	All references to manufacturer's model numbers and other pertinent information herein is intended to establish minimum standards of performance, function and quality. Equivalent compatible UL-listed equipment from other manufacturers may be substituted for the specified equipment as long as the minimum standards are met.

3.	For equipment other than that specified, the contractor shall supply proof that such substitute equipment equals or exceeds the features, functions, performance, and quality of the specified equipment.

B.	Shop Drawings:

1.	Sufficient information, clearly presented, shall be included to determine compliance with drawings and specifications.

2.	Include manufacturer's name(s), model numbers, ratings, power requirements, equipment layout, device arrangement, complete wiring point-to-point diagrams, and conduit layouts.

3.	Show annunciator layout, configurations, and terminations.

C.	Manuals:

1.	Submit simultaneously with the shop drawings, complete operating and maintenance manuals listing the manufacturer's name(s), including technical data sheets.

2.	Wiring diagrams shall indicate internal wiring for each device and the interconnections between the items of equipment.

3.	Provide a clear and concise description of operation that gives, in detail, the information required to properly operate the equipment and system.

D.	Software Modifications

1.	Provide the services of a qualified technician to perform all system software modifications, upgrades or changes.  Response time of the technician to the site shall not exceed 4 hours.

2.	Provide all hardware, software, programming tools and documentation necessary to modify the fire alarm system on site. Modification includes addition and deletion of devices, circuits, zones and changes to system operation and custom label changes for devices or zones. The system structure and software shall place no limit on the type or extent of software modifications on-site. Modification of software shall not require power-down of the system or loss of system fire protection while modifications are being made.

E.	Certifications:

Together with the shop drawing submittal, submit a certification from the major equipment manufacturer indicating that the proposed supervisor of the installation and the proposed performer of contract maintenance is an authorized representative of the major equipment manufacturer. Include names and addresses in the certification.

1.4.	GUARANTY:

All work performed and all material and equipment furnished under this contract shall be free from defects and shall remain so for a period of at least one (1) year from the date of acceptance. The full cost of maintenance, labor and materials required to correct any defect during this one year period shall be included in the submittal bid.

1.5.	MAINTENANCE:

A.	Maintenance and testing shall be on a semi-annual schedule or as required by the local AHJ. The contractor shall provide a preventive maintenance schedule describing the protocol for preventive maintenance. The schedule shall include:

1.	Systematic examination, adjustment and cleaning of all detectors, manual fire alarm stations, control panels, power supplies, relays, waterflow switches and all accessories of the fire alarm system.

2.	Each circuit in the fire alarm system shall be tested semiannually.

3.	Each smoke detector shall be tested in accordance with the requirements of NFPA 72 Chapter 7.

B.	As part of the bid/proposal, a separate quote for a maintenance contract to provide all maintenance, tests, and repairs described below. Include also a quote for unscheduled maintenance/repairs, including hourly rates for technicians trained on this equipment, and response travel costs for each year of the maintenance period. Submittals shall identify all post contract maintenance costs will be provided. Rates and costs shall be valid for the period of five (5) years after expiration of the guaranty.

1.6.	POST CONTRACT EXPANSIONS:

A.	The contractor shall have the ability to provide parts and labor to expand the system specified, if so requested, for a period of five (5) years from the date of acceptance.

B.	As part of the submittal, a separate quotation for all parts and material, and all installation and test labor as needed to increase the number of intelligent or addressable devices by ten percent (10%). This quotation shall include intelligent smoke detectors, intelligent heat detectors, addressable manual stations, addressable monitor modules and addressable control modules equal in number to one tenth of the number required to meet this specification (list actual quantity of each type).

C.	The quotation (if provided)  shall include installation, test labor, and labor to reprogram the system for this 10% expansion. If additional FACP hardware is required, include the material and labor necessary to install this hardware.

D.	Not included is the cost of conduit or wire or the cost to install conduit or wire except for labor to make final connections at the FACP and at each intelligent addressable device. Do not include the cost of conventional peripherals or the cost of initiating devices or notification appliances connected to the addressable monitor/control modules.

E.	Submittals that do not include this estimate of post contract expansion cost may be submitted.

1.7.	APPLICABLE STANDARDS AND SPECIFICATIONS:

The specifications and standards listed below form a part of this specification. The system shall fully comply with the latest issue of these standards, if applicable.

A.	National Fire Protection Association (NFPA) - USA:

No. 13	Sprinkler Systems

No. 70	National Electric Code (NEC)

No. 72	National Fire Alarm Code

No. 101	Life Safety Code

B.	The system and its components shall be Underwriters Laboratories, Inc. listed under the appropriate UL testing standard as listed herein for fire alarm applications and the installation shall be in compliance with the UL listing.

C.	Local and State Building Codes.

D.	All requirements of the Authority Having Jurisdiction (AHJ).

1.8.	APPROVALS:

A.	The system shall have proper listing and/or approval from the following nationally recognized agencies:

UL	Underwriters Laboratories Inc

1.	The FACP shall be capable of coding Notification Appliance Circuits in March Time Code (120 PPM), Temporal (NFPA 72 A-2-2.2.2), and California Code. Main panel notification circuits (NACs 1 & 2) shall also automatically synchronize notification appliances connected to them.

B.	Central Microprocessor

1.	The microprocessor shall be a state-of-the-art, high speed, 16-bit RISC device and it shall communicate with, monitor and control all external interfaces. It shall include an EPROM for system program storage, non-volatile memory for building-specific program storage, and a "watch dog" timer circuit to detect and report microprocessor failure.

2.	The microprocessor shall contain and execute all specific actions to be taken in the condition of an alarm. Control programming shall be held in non-volatile programmable memory, and shall not be lost even if system primary and secondary power failure occurs.

3.	The microprocessor shall also provide a real-time clock for time annotation of system displays, printer, and history file.

4.	A special program check function shall be provided to detect common operator errors.

5.	An auto-programming capability (self-learn) shall be provided to quickly identify devices connected on the SLC and make the system operational.

6.	For flexibility and to ensure program validity, an optional Windows(TM) based program utility shall be available. This program shall be used to off-line program the system with batch upload/download. This program shall also have a verification utility, which scans the program files, identifying possible errors. It shall also have the ability to compare old program files to new ones, identifying differences in the two files to allow complete testing of any system operating changes. This shall be in incompliance with the NFPA 72 requirements for testing after system modification.

C.	Local Keyboard Interface

1.	In addition to an integral keypad, the fire alarm control panel will accept a standard PS2-style keyboard for programming, testing, and control of the system. The keyboard will be able to execute the system functions ACKNOWLEDGE, SIGNALS SILENCED, DRILL and RESET.

D.	Display

1.	The display shall provide all the controls and indicators used by the system operator and may also be used to program all system operational parameters.

2.	The display shall include status information and custom alphanumeric labels for all intelligent detectors, addressable modules, internal panel circuits, and software zones.

3.	The display shall contain an alphanumeric, text-type display and dedicated LEDs for the annunciation of AC POWER, FIRE ALARM, SUPERVISORY, TROUBLE, MAINTENANCE, ALARM SILENCED, DISABLED, BATTERY, and GROUND conditions.

4.	The display keypad shall be part of the standard system and have the capability to command all system functions, entry of any alphabetic or numeric information, and field programming. Two different password levels shall be provided to prevent unauthorized system control or programming.

5.	The display shall include the following operator control switches: ACKNOWLEDGE, ALARM SILENCE, DRILL (alarm activate), and SYSTEM RESET.

E.	Signaling Line Circuit (SLC)

1.	The SLC interface shall provide power to and communicate with up to 99 intelligent detectors (ionization, photoelectric or thermal) and 99 intelligent modules (monitor or control) for a system capacity of 198 devices. Each SLC shall be capable of NFPA 72 Style 4, Style 6, or Style 7 (Class A or B) wiring.

2.	The CPU shall receive information from all intelligent detectors to be processed to determine whether normal, alarm, prealarm, or trouble conditions exist for each detector. The software shall automatically compensate for the accumulation of dust in each detector up to allowable limits. The information shall also be used for automatic detector testing and for the determination of detector maintenance conditions.

3.	The detector software shall meet NFPA 72, Chapter 7 requirements and be certified by UL as a calibrated sensitivity test instrument.

F.	Serial Interfaces

1.	The system shall provide a means of interfacing to UL Listed Electronic Data Processing (EDP) peripherals using the EIA-232 communications standard.

G.	The control panel will have the capability of Reverse Polarity Transmission or connection to a Municipal Box for compliance with applicable NFPA standards.

H.	Digital Alarm Communicator Transmitter (DACT). The DACT is an interface for communicating digital information between a fire alarm control panel and an UL-Listed central station.

1.	The DACT shall be an integral component of the fire alarm control panel requiring no interconnecting wiring or supervisory circuitry.

2.	The DACT shall include connections for dual telephone lines (with voltage detect), per UL/NFPA/FCC requirements. It shall include the ability for split reporting of panel events up to three different telephone numbers.

3.	The DACT shall be completely fielded programmable locally from a control panel keypad or remotely over a phone line using upload/download PC software.

4.	The DACT shall be capable of transmitting events in at least 15 different formats. This ensures compatibility with existing and future transmission formats.

5.	Communication shall include vital system status such as:

-	Independent Zone (Alarm, trouble, non-alarm, supervisory)

-	Independent Addressable Device Status

-	AC (Mains) Power Loss

-	Low Battery and Earth Fault

-	System Off Normal

-	12 and 24-Hour Test Signal

-	Abnormal Test Signal (per UL requirements)

-	EIA-485 Communications Failure

-	Phone Line Failure

6.	The DACT shall support independent zone/point reporting when used in the Contact ID format. In this format, the DACT shall support the transmission of up addressable points with the system. This enables the central station to have exact details concerning the origin of the fire or response emergency.

I.	Stand Alone Voice Evacuation Control Panel

1.	A stand-alone Voice Evacuation Control Panel shall be available from the same manufacturer of the main fire alarm system.

2.	This Voice Control Panel shall work stand alone or as a slave to the Main Fire Alarm Control Panel.

3.	Shall have as minimum requirements:

a.	Integral 25 Watt, 25 Vrms audio amplifier.

b.	Speaker circuit that can be wired both Class A or B.

c.	Integral Digital Message Generator with a memory capacity for up to 60 seconds of messaging.  The Digital Message Generator shall be capable of producing five distinct messages (12 seconds each).  These messages shall field programmable without the use of additional equipment.

d.	Built in alert tone generators with steady, slow whoop, high/low and chime tone field programmable.

e.	The Voice Control Panel will be capable of detecting and annunciating the following conditions: Loss of Power (AC and DC), System Trouble, Ground Fault, Alarm, Microphone Trouble, Message Generator Trouble, Tone Generator Trouble, and Amplifier Fault.

4.	The Voice Control Panel shall be fully supervised including microphone, amplifier output, message generator, speaker wiring, and tone generation.

5.	Speaker outputs shall be fully power-limited.

6.	Amplifiers will be supplied power independently to eliminate a short on one circuit from affecting other circuits.

7.	The Voice Control Panel will provide full supervision on both active  (alarm or music) and standby conditions.

J.	Speakers:

1.	All speakers shall operate on 25 VRMS or with field selectable output taps from 0.5 to 2.0 Watts.

2.	Speakers in corridors and public spaces shall produce a nominal sound output of 84 dBA at 10 feet (3m).

3.	Frequency response shall be a minimum of 400 HZ to 4000 HZ.

4.	The back of each speaker shall be sealed to protect the speaker cone from damage and dust.

K.	Enclosures:

1.	The control panel shall be housed in an UL-listed cabinet suitable for surface or semi-flush mounting. The cabinet and front shall be corrosion protected, given a rust-resistant prime coat, and manufacturer's standard finish.

2.	The back box and door shall be constructed of steel with provisions for electrical conduit connections into the sides and top.

3.	The door shall provide a key lock and shall provide for the viewing of all indicators.

4.	One EIA-232 interface shall be used to connect an UL-Listed 80-column printer. The printer shall communicate with the control panel using an interface complying with Electrical Industries Association standard EIA-232D. Power to the printer shall be 120 VAC @ 60 Hz.

L.	Field Charging Power Supply: The FCPS is a device designed for use as either a remote 24-volt power supply or as a booster for powering Notification Appliances.

1.	The FCPS shall offer up to 8.0 amps (6.0 amps continuous) of regulated 24-volt power. It shall include an integral charger designed to charge 18.0 amp hour batteries.

2.	The Field Charging Power Supply shall have two input triggers. The input trigger shall be a Notification Appliance Circuit (from the fire alarm control panel) or a control relay. Four NAC outputs, wired NFPA Style Y or Z, shall be available for connection to the Notification devices.

3.	The FCPS shall synchronize the activation of all connected strobes.

4.	The FCPS shall function as a sync follower as well as a sync generator.

5.	The FCPS shall include a surface mount back box.

6.	The Field Charging Power Supply shall include the ability to delay the reporting of an AC fail condition per NFPA requirements.

7.	The FCPS shall provide 24 VDC regulated and power-limited circuitry per 1995 UL standards.

M.	Power Supply:

1.	The main power supply for the fire alarm control panel shall provide 6.0 amps of available power for the control panel and peripheral devices.

2.	Provisions will be made to allow the audio-visual power to be increased as required by adding modular expansion audio-visual power supplies.

3.	Positive-Temperature-Coefficient (PTC) thermistors, circuit breakers, or other over-current protection shall be provided on all power outputs. The power supply shall provide an integral battery charger or may be used with an external battery and charger systems. Battery arrangement may be configured in the field.

4.	The main power supply shall continuously monitor all field wires for earth ground conditions.

5.	The main power supply shall be wired to a customer provided, dedicated  120 VAC, 20 Amp. 60 Hz, branch circuit, with circuit breaker and breaker lock, and shall provide all necessary power for the FACP.

N.	Programmable Electronic Sounders:

1.	Electronic sounders shall operate on 24 VDC nominal.

2.	Electronic sounders shall be field programmable without the use of special tools, to provide slow whoop, continuous, or interrupted tones with an output sound level of at least 90 dBA measured at 10 feet from the device.

3.	Shall be flush or surface mounted as show on plans.

O.	Strobe lights shall meet the requirements of the ADA, UL Standard 1971 and shall meet the following criteria:

1.	The maximum pulse duration shall be 2/10 of one second+d.

2.	Strobe intensity shall meet the requirements of UL 1971.

3.	The flash rate shall meet the requirements of UL 1971.

P.	Audible/Visual Combination Devices:

1.	Shall meet the applicable requirements of Section A listed above for audibility.

2.	Shall meet the requirements of Section B listed above for visibility.

Q.	Manual Fire Alarm Stations

1.	Manual fire alarm stations shall be non-code, non-break glass type, equipped with key lock so that they may be tested without operating the handle.

2.	Stations must be designed such that after an actual activation, they cannot be restored to normal except by key reset.

3.	An operated station shall automatically condition itself so as to be visually detected, as operated, at a minimum distance of 100 feet (30.5 m) front or side.

4.	Manual stations shall be constructed of high impact Lexan, with operating instructions provided on the cover. The word FIRE shall appear on the manual station in letters one half inch (12.7 mm) in size or larger.

R.	Manual Fire Alarm Stations

1.	Manual fire alarm stations shall be non-code, non-break glass type, equipped with key lock so that they may be tested without operating the handle.

2.	Stations must be designed such that after an actual activation, they cannot be restored to normal except by key reset.

3.	An operated station shall automatically condition itself so as to be visually detected, as operated, at a minimum distance of 100 feet (30.5 m) front or side.

4.	Manual stations shall be constructed of sturdy metal construction, with operating instructions provided on the cover. The word FIRE shall appear on the manual station in letters one half inch (12.7 mm) in size or larger.

S.	Conventional Photoelectric Area Smoke Detectors

1.	Photoelectric smoke detectors shall be a 24 VDC, two wire, ceiling-mounted, light scattering type using an LED light source.

2.	Each detector shall contain a remote LED output and a built-in test switch.

3.	The detector shall be of a separate head-in-base design.

4.	The detector shall automatically provide drift compensation to minimize nuisance alarms.

5.	The detector shall be capable of generating a signal when maintenance is required.

6.	It shall be possible to read the sensitivity of the device in percent obscuration per foot without the need for the generation of smoke.

7.	A visual indication of an alarm shall be provided by dual latching Light Emitting Diodes (LEDs), on the detector, which may be seen from ground level over 360 degrees. These LEDs shall flash every 5 seconds, indicating that power is applied to the detector.

8.	The detector shall not go into alarm when exposed to air velocities of up to 3000 feet (914.4 m) per minute.

9.	The detector screen and cover assembly shall be easily removable for field cleaning of the detector chamber.

10.	All field wire connections shall be made to the base through the use of a clamping plate and screw.

T.	Conventional Ionization Type Area Smoke Detectors

1.	Ionization type smoke detectors shall be a two wire, 24 VDC type using a dual unipolar chamber.

2.	Each detector shall contain a remote LED output and a built-in test switch.

3.	Detector shall be provided on a twist-lock base.

4.	It shall be possible to perform a calibration sensitivity and performance test on the detector without the need for the generation of smoke.

5.	A visual indication of an alarm shall be provided by dual latching Light Emitting Diodes (LEDs) over 360 degrees, on the detector, which may be seen from ground level. This LED shall flash every 10 seconds, indicating that power is applied to the detector.

6.	The detector shall not alarm when exposed to air velocities of up to 1,200 feet (365.76 m) per minute. The detector screen and cover assembly shall be easily removable for field cleaning of the detector chamber.

7.	All field wire connections shall be made to the base through the use of a clamping plate and screw.

U.	Duct Smoke Detectors

Duct smoke detectors shall be a 24 VDC type with visual alarm and power indicators, and a reset switch. Each detector shall be installed upon the composite supply/return air ducts(s), with properly sized air sampling tubes.

V.	Projected Beam Detectors

1.	The projected beam type shall be a 4-wire 24 VDC device.

2.	The detector shall be listed to UL 268 and shall consist of a separate transmitter and receiver capable of being powered separately or together.

3.	The detector shall operate in either a short range (30' - 100') or long range (100' - 330') mode.

4.	The temperature range of the device shall be -22 degrees F to 131 degrees F.

5.	The detector shall feature a bank of four alignment LEDs on both the receiver and the transmitter that are used to ensure proper alignment of unit without special tools.

6.	Beam detector shall feature automatic gain control, which will compensate for gradual signal deterioration from dirt accumulation on lenses.

7.	The unit shall be both ceiling and wall mountable.

8.	The detector shall have the ability to be tested using calibrated test filters or magnet-activated remote test station.

W.	Automatic Conventional Heat Detectors

1.	Automatic heat detectors shall have a combination rate of rise and fixed temperature rated at 135 degrees Fahrenheit (57.2 Celsius) for areas where ambient temperatures do not exceed 100 degrees (37.7 Celsius), and 200 degrees (93.33 Celsius) for areas where the temperature does not exceed 150 degrees (65.5 Celsius).

2.	Automatic heat detectors shall be a low profile, ceiling mount type with positive indication of activation.

3.	The rate of rise element shall consist of an air chamber, a flexible metal diaphragm, and a factory calibrated, moisture-proof, trouble free vent, and shall operate when the rate of temperature rise exceeds 15 degrees F (9.4 degrees C) per minute.

4.	The fixed temperature element shall consist of a fusible alloy retainer and actuator shaft.

5.	Automatic heat detectors shall have a smooth ceiling rating of 2500 square feet (762 square meters).

X.	Waterflow Indicator:

1.	Waterflow Switches shall be an integral, mechanical, non-coded, non-accumulative retard type.

2.	Waterflow Switches shall have an alarm transmission delay time, which is conveniently adjustable from 0 to 60 seconds. Initial settings shall be 30-45 seconds.

3.	All water flow switches shall come from a single manufacturer and series.

4.	Waterflow switches shall be provided and connected under this section but installed by the mechanical contractor.

5.	Where possible, locate water flow switches a minimum of one (1) foot from a fitting, which changes the direction of the flow and a minimum of three (3) feet from a valve.

Y.	Sprinkler and Standpipe Valve Supervisory Switches:

1.	Each sprinkler system water supply control valve riser, zone control valve, and standpipe system riser control valve shall be equipped with a supervisory switch. Standpipe hose valves, and test and drain valves shall not be equipped with supervisory switches.

2.	PIV (post indicator valve) or main gate valves shall be equipped with a supervisory switch.

3.	The switch shall be mounted so as not to interfere with the normal operation of the valve and adjusted to operate within two revolutions toward the closed position of the valve control, or when the stem has moved no more than one-fifth of the distance from its normal position.

4.	The supervisory switch shall be contained in a weatherproof aluminum housing, which shall provide a 3/4-inch (19 mm) conduit entrance and incorporate the necessary facilities for attachment to the valves.

5.	The switch housing shall be finished in red baked enamel.

6.	The entire installed assembly shall be tamper proof and arranged to cause a switch operation if the housing cover is removed, or if the unit is removed from its mounting.

7.	Valve supervisory switches shall be provided and connected under this section and installed by mechanical contractor.

Z.	Specific System Operations

1.	Alarm Verification: Each of the intelligent addressable smoke detectors in the system may be independently programmed for verification of alarm signals. The alarm verification time period shall not exceed 2 minutes.

2.	Point Disable: Any addressable device or conventional circuit in the system may be enabled or disabled through the system keypad.

3.	Point Read: The system shall be able to display the following point status diagnostic functions:

a.	Device status

b.	Device type

c.	Custom device label

d.	Device zone assignments

4.	System Status Reports: Upon command from an operator of the system, a status report will be generated and printed, listing all system status.

5.	System History Recording and Reporting: The fire alarm control panel shall contain a history buffer that will be capable of storing up to 1000 events. Each of these activations will be stored and time and date stamped with the actual time of the activation. The contents of the history buffer may be manually reviewed, one event at a time, or printed in its entirety.

The history buffer shall use non-volatile memory. Systems that use volatile memory for history storage are not acceptable substitutes.

6.	Automatic Detector Maintenance Alert: The fire alarm control panel shall automatically interrogate each intelligent detector and shall analyze the detector responses over a period of time. If any intelligent detector in the system responds with a reading that is above or below normal limits, then the system will enter the trouble mode, and the particular detector will be annunciated on the system display.  This feature shall in no way inhibit the receipt of alarm conditions in the system, nor shall it require any special hardware, special tools or computer expertise to perform.

7.	Pre-Alarm Function: The system shall provide two levels of pre-alarm warning to give advance notice of a possible fire situation. Both pre-alarm levels shall be fully field adjustable. The system shall also have the ability to activate local detector sounder bases at the pre-alarm level, to assist in avoiding nuisance alarms.

8.	The fire alarm control panel shall include Silent and Audible Walk Test functions - Silent and Audible. It shall include the ability to test initiating device circuits and Notification Appliance Circuits from the field without returning to the panel to reset the system. The operation shall be as follows:

a	The Silent Walk Test will not sound NACs but will store the Walk Test information in History for later viewing.

b.	Alarming an initiating device shall activate programmed outputs, which are selected to participate in Walk Test.

c.	Introducing a trouble into the initiating device shall activate the programmed outputs.

d.	Walk Test shall be selectable on a per device/circuit basis. All devices and circuits, which are not selected for Walk Test, shall continue to provide fire protection and if an alarm is detected, will exit Walk Test and activate all programmed alarm functions.

e.	All devices tested in walk test shall be recorded in the history buffer.

9.	Waterflow Operation

An alarm from a water flow detection device shall activate the appropriate alarm message on the control panel display; turn on all programmed Notification Appliance Circuits and shall not be affected by the Signal Silence switch.

10.	Supervisory Operation

An alarm from a supervisory device shall cause the appropriate indication on the control panel display, light a common supervisory LED, but will not cause the system to enter the trouble mode.

11.	Signal Silence Operation

The FACP shall have the ability to program each output circuit (notification circuit or relay) to deactivate upon depression of the Signal Silence switch.

12.	Non-Alarm Input Operation

Any addressable initiating device in the system may be used as a non-alarm input to monitor normally open contact type devices. Non-alarm functions are a lower priority than fire alarm initiating devices.

1.9.	SYSTEM COMPONENTS:

A. 	Addressable Pull Box (manual station)

1.	Addressable pull boxes shall, on command from the control panel, send data to the panel representing the state of the manual switch and the addressable communication module status. They shall use a key operated test-reset lock, and shall be designed so that after actual emergency operation, they cannot be restored to normal use except by the use of a key.

2.	All operated stations shall have a positive, visual indication of operation and utilize a key type reset.

3.	Manual stations shall be constructed of Lexan with clearly visible operating instructions provided on the cover. The word FIRE shall appear on the front of the stations in raised letters, 1.75 inches (44 mm) or larger.

B.	Intelligent Multi-Sensing Detector

1.	The intelligent detector shall be an addressable device, which is capable of detecting multiple threats by employing photoelectric and thermal technologies in a single unit.  This detector shall utilize advanced electronics, which react to slow smoldering fires (photoelectric) and heat (thermal) all within a single sensing device.

2.	The multi-detector shall include two bicolor LEDs for 360-degree viewing.

3	Automatically adjusts sensitivity levels without the need for operator intervention or programming. Sensitivity increases with heat.

C.	Intelligent Photoelectric Smoke Detector

1.	The detectors shall use the photoelectric (light-scattering) principal to measure smoke density and shall, on command from the control panel, send data to the panel representing the analog level of smoke density.

2.	The detectors shall be ceiling-mounted and available in an alternate model with an integral fixed 135-degree heat-sensing element.

3.	Each detector shall contain a remote LED output and a built-in test switch.

4.	Detector shall be provided on a twist-lock base.

5.	It shall be possible to perform a calibrated sensitivity and performance test on the detector without the need for the generation of smoke.  The test method shall test all detector circuits.

6.	A visual indication of an alarm shall be provided by dual latching Light Emitting Diodes (LEDs), on the detector, which may be seen from ground level over 360 degrees. These LEDs shall periodically flash to indicate that the detector is in communication with the control panel.

7.	The detector shall not go into alarm when exposed to air velocities of up to 1500 feet per minute (fpm).

8.	The detector screen and cover assembly shall be easily removable for field cleaning of the detector chamber.

9.	All field wire connections shall be made to the base through the use of a clamping plate and screw.

D.	Intelligent Ionization Smoke Detector

1.	The detectors shall use the dual-chamber ionization principal to measure products of combustion and shall, on command from the control panel, send data to the panel representing the analog level of products of combustion.

E.	Intelligent Thermal Detectors

1.	Thermal detectors shall be intelligent addressable devices rated at 135 degrees Fahrenheit (58 degrees Celsius) and have a rate-of-rise element rated at 15 degrees F (9.4 degrees C) per minute. It shall connect via two wires to the fire alarm control panel signaling line circuit.

F.	Intelligent Duct Smoke Detector

1.	The smoke detector housing shall accommodate either an intelligent ionization detector or an intelligent photoelectric detector, of that provides continuous analog monitoring and alarm verification from the panel.

2.	When sufficient smoke is sensed, an alarm signal is initiated at the FACP, and appropriate action taken to change over air handling systems to help prevent the rapid distribution of toxic smoke and fire gases throughout the areas served by the duct system.

G.	Addressable Dry Contact Monitor Module

1.	Addressable monitor modules shall be provided to connect one supervised IDC zone of conventional alarm initiating devices (any normally open dry contact device) to one of the fire alarm control panel SLC’s.

2.	The monitor module shall mount in a 4-inch square (101.6 mm square), 2-1/8 inch (54 mm) deep electrical box.

3.	The IDC zone shall be suitable for Style D or Style B operation. An LED shall be provided that shall flash under normal conditions, indicating that the monitor module is operational and in regular communication with the control panel.

4.	For difficult to reach areas, the monitor module shall be available in a miniature package and shall be no larger than 2-3/4 inch (70 mm) x 1-1/4 inch (31.7 mm) x 1/2 inch (12.7 mm). This version need not include Style D or an LED.

H.	Two-Wire Detector Monitoring

1.	Means shall be provided for the monitoring of conventional Initiating Device Circuits populated with 2-wire smoke detectors as well as normally open contact alarm initiating devices (pull stations, heat detectors, etc).

2.	Each IDC of conventional devices will be monitored as a distinct address on the polling circuit by an addressable module.  The module will supervise the IDC for alarms and circuit integrity (opens).

3.	The monitoring module will be compatible, and listed as such, with all devices on the supervised circuit.

4.	The IDC zone may be wired for Class A or B (Style D or Style B) operation. An LED shall be provided that shall flash under normal conditions, indicating that the monitor module is operational and in regular communication with the control panel.

5.	The monitoring module shall be capable of mounting in a 4-inch square (101.6 mm square), 2-1/8 inch (54 mm) deep electrical box or in a surface mount back box.

I.	Addressable Control Module

1.	Addressable control modules shall be provided to supervise and control the operation of conventional Notification Appliance Circuits (NACs) of compatible, 24 VDC powered, polarized audio/visual notification appliances.

2.	The control module shall mount in a standard 4-inch square, 2-1/8 inch deep electrical box, or to a surface mounted back box.

3.	The control module NAC may be wired for Style Z or Style Y (Class A/B) with up to 1 amp of inductive A/V signal, or 2 amps of resistive A/V signal operation.  The relay coil shall be magnetically latched to reduce wiring connection requirements, and to insure that 100% of all NACs may be energized at the same time on the same pair of wires.

4.	Audio/visual power shall be provided by a separate supervised power circuit from the main fire alarm control panel or from a supervised, UL listed remote power supply.

J.	Addressable Control Relay Module

1.	Addressable control relay modules shall be provided to control the operation of fan shutdown and other auxiliary control functions.

2.	The control module shall mount in a standard 4-inch square, 2-1/8 inch deep electrical box, or to a surface mounted back box.

3.	The control relay module will provide a dry contact, Form-C relay. The relay coil shall be magnetically latched to reduce wiring connection requirements, and to insure that 100% of all auxiliary relays may be energized at the same time on the same pair of wires.

4.	The control relay module shall be suitable for pilot duty applications and rated for a minimum of 0.6 amps at 30 VDC.

K.	Isolator Module

1.	Isolator modules shall be provided to automatically isolate wire-to-wire short circuits on an SLC Style 6 (Class A) or Style 4 (Class B branch). The isolator module shall limit the number of modules or detectors that may be rendered inoperative by a short circuit fault on the SLC loop segment or branch. At least one isolator module shall be provided for each floor or protected zone of the building.

2.	If a wire-to-wire short occurs, the isolator module shall automatically open-circuit (disconnect) the SLC. When the short circuit condition is corrected, the isolator module shall automatically reconnect the isolated section.

3.	The isolator module shall not require any address setting, and its operations shall be totally automatic. It shall not be necessary to replace or reset an isolator module after its normal operation.

4.	The isolator module shall mount in a standard 4-inch (101.6 mm) deep electrical box or in a surface mounted back box. It shall provide a single LED that shall flash to indicate that the isolator is operational and shall illuminate steadily to indicate that a short circuit condition has been detected and isolated.

L.	Serially Connected Annunciator

1.	The annunciator shall communicate with the fire alarm control panel via a two wire EIA 485 (multi-drop) communications circuit.

2.	The annunciator shall require no more than four wires for operation. Annunciation shall include: intelligent addressable points, system software zones, control relays, and notification appliance circuits. The following operations shall also be provided:

a.	Up to 32 annunciators, each with up to 64 points may be installed on the system.

b.	The annunciator shall include a single electrical key switch to disable all switch functions.

c.	The annunciator shall provide alarm and trouble resound, with flash for new conditions.

M.	Door Holders:

1.	Door Holders will be available in 120 VAC and 24 VDC models.

2.	120 VAC models will be transient-protected against surges up to 600 volts.

3.	Door holders will be designed for Fail Safe operation (power failure release door to close).

N.	Elevator Recall:

1.	Smoke detectors will be installed in the elevator hoist shaft.  An alarm from such devices will signal the elevator to initiate emergency procedures.  All lift call buttons; door buttons and signals will become inoperative in the lift bank serving the machine room.  Lifts will immediately be sent to the main floor of egress (ground level) where they will be decommissioned until the alarm condition has been cleared or manually taken over by Fire Department personnel.

2	Smoke detectors will be installed in each elevator lobby.  These detectors will function to signal the elevator to recall to the primary floor of egress (ground level) in the event of an alarm.  Detectors on the first floor will signal the elevator to recall to the secondary floor of egress.

O.	Field Wiring Terminal Blocks

For ease of service all panel I/O wiring terminal blocks shall be removable, plug-in types and have sufficient capacity for #18 to #12 AWG wire. Terminal blocks, which are permanently fixed, are not acceptable.

1.10.	SYSTEM COMPONENTS - ADDRESSABLE DEVICES

A.	Addressable Devices - General

1.	Addressable devices shall employ the simple-to-set decade addressing scheme.  Addressable devices, which use a binary-coded address setting method, such as a DIPswitch, are not an allowable substitute.

2.	Detectors shall be addressable and intelligent, and shall connect with two wires to the fire alarm control panel signaling line circuits.

3.	Addressable smoke and thermal (heat) detectors shall provide dual alarm and power/polling LEDs. Both LEDs shall flash under normal conditions, indicating that the detector is operational and in regular communication with the control panel, and both LEDs shall be placed into steady illumination by the control panel, indicating that an alarm condition has been detected. An output connection shall also be provided in the base to connect an external remote alarm LED.

4.	Using software in the FACP, detectors shall automatically compensate for dust accumulation and other slow environmental changes that may affect their performance. The detectors shall be listed by UL as meeting the calibrated sensitivity test requirements of NFPA Standard 72, Chapter 7.

5.	Detectors shall be ceiling-mount and shall include a separate twist-lock base with tamper proof feature. Base options shall include a base with a built-in (local) sounder rated for a minimum of 85 DBA, a relay base and an isolator base designed for Style 7 applications.

6.	Detectors shall provide a test means whereby they will simulate an alarm condition and report that condition to the control panel.

7.	Detectors shall also store an internal identifying type code that the control panel shall use to identify the type of device (ION, PHOTO, THERMAL).

8.	Detectors shall provide address-setting means using decimal switches.

1.11.	BATTERIES:

A.	Upon loss of Primary (AC) power to the control panel, the batteries shall have sufficient capacity to power the fire alarm system for required standby time (24 or 60 hours) followed by 5 minutes of alarm.

B.	The batteries are to be completely maintenance free. No liquids are required. Fluid level checks for refilling, spills, and leakage shall not be required.

C.	If necessary to meet standby requirements, external battery/charger systems may be used.

# PART 2.0 - EXECUTION

3.1.	INSTALLATION:

A.	Installation shall be in accordance with the NEC, NFPA 72, local and state codes, as shown on the drawings, and as recommended by the major equipment manufacturer. All work shall be by licensed technicians of Patriot Alarm Systems Inc.

B.	All conduit, junction boxes, conduit supports and hangers shall be concealed in finished areas and may be exposed in unfinished areas. Smoke detectors shall not be installed prior to the system programming and test period. If construction is ongoing during this period, measures shall be taken to protect smoke detectors from contamination and physical damage.

C.	All fire detection and alarm system devices, control panels and remote annunciators shall be flush mounted when located in finished areas and may be surface mounted when located in unfinished areas.

D.	Manual pull stations shall be suitable for surface mounting or semi flush mounting as shown on the plans, and shall be installed not less than 42 inches (1067 mm), nor more than 48 inches (122 mm) above the finished floor.

3.2.	TEST:

The service of a competent, factory-trained engineer or technician authorized by the manufacturer of the fire alarm equipment shall be provided to technically supervise and participate during all of the adjustments and tests for the system. All testing shall be in accordance with NFPA 72, Chapter 7.

A.	Before energizing the cables and wires, check for correct connections and test for short circuits, ground faults, continuity, and insulation.

B.	Close each sprinkler system flow valve and verify proper supervisory alarm at the FACP.

C.	Verify activation of all water flow switches.

D.	Open initiating device circuits and verify that the trouble signal actuates.

E.	Open and short signaling line circuits and verify that the trouble signal actuates.

F.	Open and short notification appliance circuits and verify that trouble signal actuates.

G.	Ground all circuits and verify response of trouble signals.

H.	Check presence and audibility of tone at all alarm notification devices.

I.	Check installation, supervision, and operation of all intelligent smoke detectors using the walk test.

J.	Each of the alarm conditions that the system is required to detect should be introduced on the system. Verify the proper receipt and the proper processing of the signal at the FACP and the correct activation of the control points.

K.	When the system is equipped with optional features, the manufacturer's manual shall be consulted to determine the proper testing procedures. This is intended to address such items as verifying controls performed by individually addressed or grouped devices, sensitivity monitoring, verification functionality and similar.

3.3.	FINAL INSPECTION:

A.	At the final inspection, a factory-trained representative of the manufacturer of the major equipment shall demonstrate that the system functions properly in every respect.

3.4.	INSTRUCTION:

A.	Instruction shall be provided as required for operating the system. Hands-on demonstrations of the operation of all system components and the entire system including program changes and functions shall be provided.

B.	The contractor and/or the systems manufacturer's representatives shall provide a typewritten "Sequence of Operation."

___________________________________                             Date: _______________

Patriot Alarm Systems Inc.

Patriot Alarm Systems Inc.

292 Bailey Street

Canton, MA 02021

781-821-2325 (Voice)       781-821-5436 (Fax )

## MA 1172          UL S-3851-1               S-3855-1

www.patriotalarm.com